Contents                                                                                                       Page

Executive summery	1

1.	INTRODCTION	2

1.1 General	2

1.2.	Specifics information of the project area	2

1.3 PROJECT GOAL AND OBJECTIVE	2

1.3.1 Goal	2

1.3.2 Objectives	2

2.	PHYSICAL CONDITIONS OF THE PROJECT AREA	3

2.1 Location	3

2.2 Accessibility	3

2.3 Topography	3

2.4 Climate, Soil and Vegetation	3

3.	SOCIO ECONOMIC CONDITION	3

3.1 Electric Supply	3

3.2 Telephone service	3

3.3 Existing Water Condition.	3

3.3.1 Project area	3

3.3.2. At the water source	3

4.	WATER DEMAND ANALYSIS	4

4.1 Population projection	4

4.1.1   Design period of the Project	4

4.1.2    Design Population	4

4.2 Water source	4

4.3 Per- capita water demand of the target area	5

4.4 Assumption and peaking factor	5

4.5 Water Demand Analysis	5

4.6 Institutional Water Demand	6

4.7.	Unaccounted water Demand	6

4.8 Reservoir capacity determination	6

5.	DESIGN OF DISTRIBUTION NET WORK and HYDRAULIC CALCULATION	7

5.1 Pressure main (from BH to 100m3 reservoir)	7

5.3 Network analysis	7

6. PUMP and GENERATOR	Error! Bookmark not defined.

6.1 General	Error! Bookmark not defined.

6.2 MAJOR ACTIVITIES	Error! Bookmark not defined.

6.3 CONCLUSION AND RECOMMENDATION	Error! Bookmark not defined.

7. BILL OF QUANTITIES	11

# Executive summery

This design report is expansion work to Awaye Keraro water supply and sanitation project, which consists Construction of Gravity line, distribution Line, water points, Construction of Anchor Blocks for Pipe Support, Network valve chamber, valve chamber for reservoir, Construction of spring caping, Construction of 100m3, 50m3 and 15m3 reservoirs. The overall cost of this project is 11,180,128.41Eth.Birr.

# INTRODCTION

## 1.1 General

The need for pure drinking water increases almost in all parts of the region. This is due to population growth, change in lively hood of target group, and others. On the other hand lack of sufficient water source and its quality, scarce investment capital and poor management condition of the scheme make the problem more serious. Therefore water supply activities require high investment capital, needs skilled man power and appropriate management system. To make the scheme sustainable and effective, supportive activities like committee establishment and appropriate, clear management strategy is obligatory for a better result.

Accesses to pure water are a serious problem manifested in all woredas of Sidama zone. Bona zuria Woreda is found in Sidam Zone and with poor water supply coverage.

Sidama Zone Water Mine and Energy department with stalk holders has made strong effort to alleviate the problem. This document comprises Socio economic condition, existing water supply coverage of bona zuria, Population projection, Demand analysis, supply and installation of pipes and fittings and construction of other civil works. Basic primary data’s were collected from bona zuria woreda Water office. Some of them are not reliable and correction was made from other sources.

## 1.2.	Specific information of the project area

The project area, awaye kararo odola Kebeles is one of the kebeles in bona zuria woreda. They have hot climatic condition and found at about 120Km away from hawassa town.

## 1.3 PROJECT GOAL AND OBJECTIVE

### 1.3.1 Goal

The goal of the project is to provide pure water and then improve the wellbeing and lively hood of the target community.

### 1.3.2 Objectives

The objectives of the proposed project are:-

- To provide safe, pure and adequate water supply,

- Improve the health status of the community by providing safe & adequate drinking water,

- Strengthen the skill & awareness of the communities towards effective and efficient utilization and management of environmental concerns (i.e. water and its sources)

- Contribute to the national development plans, Universal Access Plan (UAP), to potable water supply.

# PHYSICAL CONDITIONS OF THE PROJECT AREA

## 2.1 Location

The project site is located in Sidama Zone, bona zuria Woreda. The area has got dense green vegetation with exotic and indigenous tree, fruit specious, perennial and annual crops.

## 2.2 Accessibility

The study area is accessible with some-weather gravel road and URAP road.

## 2.3 Topography

The topography is gentle slope, steep, medium and it varies. The potential expansion areas of the town are even more than the above ranges.

## 2.4 Climate, Soil and Vegetation

Meteorological data is not found as a result of absence of the station, however it has got cold humid climatic condition and the soil is dominantly clay. The type of vegetation found are predominantly exotic and some indigenous and other perennial crops like ‘’Enset”.

# SOCIO ECONOMIC CONDITION

## 3.1 Electric Supply

There is electric power supply at the kebele town and around the project site.

## 3.2 Telephone service

The project area is provided with telephone service. For the mobile telephone network coverage is available at all parts of the Project area.

## 3.3 Existing Water Condition.

### 3.3.1 Project area

The target community supplied with spring and hand pumps fitted with pump.

### 3.3.2. At the water source

The potential water source is Bore hole located at abaye kararo odola kebele. The spring was designed to serves as a domestic water source and hygienic purpose to the surrounding community.

# WATER DEMAND ANALYSIS

## 4.1 Population projection

### 4.1.1   Design period of the Project

The economic design period of water supply structures depends up on material life, investment cost (first cost), ease of expansion and others. New water supply schemes are made large enough to meet the needs of the growing population for an economically justifiable number of years in the future. Thus, the design period of a water supply scheme should neither be too long that the present population of the target community is over taxed nor should be too small that just after a few years it may require large extensions due to the increased water requirements. So 20 years of design period is selected for this project.

### 4.1.2    Design Population

There are a numbers of methods to be used to forecast the future population to be served by the proposed water supply system. But, it should be judged to select among various methods of forecasting future population. The basic growth rate for domestic water demand calculation is Central Statistical Authority (CSA) is used. Growth rate and population of Targeted area are 3% and 6150 respectively. There for assuming 3% annual growth rate, using geometric increase method, and considering 2009 E.C as a base year population is projected for every five years intervals as:-

Pn = Po (1+r) t

Where: -	 Pn = Future population with in the design period

Po = Existing population

r = Annual percentage growth rate

t = the design period in years

Using the above parameters, future population is projected for every five years intervals up to the design period of project and tabulated as follows.

## 4.2 Water source

The water source is spring found at a higher elevation. As the design criteria indicates that the water source capacity needs to be sized for the total water demand including unaccounted for water. The spring yield 1.5l/s was measured.

## 4.3 Per- capita water demand of the target area

Per – capita water demand depends on the availability of other water sources in the surrounding area, climatic factor, quality of water, system of water supply, and other. So, per - capita water demand for these Kebeles is assumed to be 25lt/capita per day.

## 4.4 Assumption and peaking factor

The following assumptions are made to design the water supply project.

- Average Water Demand:-

Average water demand is obtained by multiplying the estimated beneficiaries at a specified year horizon with the total corresponding projected per capita water demand.

- Maximum Day Demand

It is a demand higher in one day of a week than in others. This condition shall be taken in to account by the use of a peak day factor of 1.2.

- Peak Hour Demand

This is due to the fact that water demand varies greatly during the day. Thus the distribution system must be designed to cope with the peak demand. The peak hour factor is expressed as a multiple of the annual average daily demand and additionally to the seasonal and peak day factor and it is 1.5.

## 4.5 Water Demand Analysis

The amount of water to be used for domestic water demand varies widely on mode of services, type & availability of water supply. The use of water for domestic purposes may be divided in to various categories as;-

- Drinking

- Cooking

- Washing

- Bath & shower

For these Kebeles domestic water demand considers all the above categories and its mode of service is using house connection and public fountains (water points). The study report considers the demand is assumed to be 25lt/capita per day.

## 4.6 Institutional Water Demand

In this project institutional water demand is not.

## Unaccounted water Demand

All the water to be produced will not be consumed due to the fact that a portion may be lost because of leakages, over flows of reservoir (s), and due to negligence on part of the dwellers. Thus, for this specific project it is considered and estimated unaccounted water demand is to be 15% of the total average daily water demand.

The population projection indicates only domestic water demand but the design needs to comprise all type of water demand including institutional, and unaccounted for use which is 2% and 15% respectively of average water demand and summarized as table below.

## 4.8 Reservoir capacity determination

In order to design the capacity of a reservoir total average daily water demand and other losses to be considered and it is presented in the following table. Since there is no demand pattern for this particular village to determine reservoir capacity and it can be determined using the rule of tomb expressed as 1/3 to ½ of the maximum day demand. As aforementioned above the present population of the target community is neither over taxed nor should be too small that just after a few years it may require large extensions due to the increased water requirements. Therefore 100m3 reservoir is required.

| Table 1.2 Population projection and water demand analysis in Awaye Keraro Community water Supply project |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Description | Growth rate per year(%) | Year |  |  |  |  |  |
|  |  | 2009 | 2010 | 2015 | 2020 | 2025 | 2030 |
| Population projection | 3 | 6150 | 6335 | 7343 | 8513 | 9869 | 11441 |
| Average per capital demand(l/c/d) |  |  | 25 | 25 | 25 | 25 | 25 |
| Average daily water demand(l/d) |  |  | 158363 | 183586 | 212826 | 246724 | 286020 |
| Maximum day demand(l/s) |  |  | 2.20 | 2.55 | 2.96 | 3.43 | 3.97 |
| Peak hourly demand(l/s) |  |  | 3.96 | 4.59 | 5.32 | 6.17 | 7.15 |
| Reservior capacity(m^3) |  |  | 53 | 61 | 71 | 82 | 95 |
| Adopted reservior capacity(m^3) |  |  | 50.00 | 75.00 | 75 | 100 | 100 |

- DESIGN OF DISTRIBUTION NET WORK and HYDRAULIC CALCULATION

## 5.1 Gravity main (from spring 50m3   WW to 100m3 reservoir)

The gravity main serves to transfer water from the spring. There are boulders and small gullies on the route of this pressure main.

The economic diameter (D) of the gravity main is:-

D = 0.9x√Q to 1.2x√Q where Q = in m3/sec. and D in m

Therefore0.0603m to 0.08049m is required

So adopt 63mm of pipe size for Q= 4.5l/sec

## 5.3 Network analysis

The distribution network will be designed on water point demand, economic size of the pipe, and future expansion.

| IN.pt | St.pt | Pipe Length | Pipe Dia (mm) | Velocity (m/s) | Discharge (l/sec) | Head loss(m) | Cum. HL | rH | Cum. rH | free Head | Node Elv. | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spring1 | 50m3 ww | 120 | 50 | 0.331 | 0.65 | 0.268 | 0.27 | -2 | -2 | 2 | 2232.00 |  |
| spring 2 | 50m3ww | 100 | 50 | 0.331 | 0.65 | 0.224 | 0.22 | -2 | -2 | 2 | 2232.00 |  |
| ww | p | 200 | 63 | 1.050 | 3.27 | 3.571 | 3.79 | -10 | -12 | 8 | 2222.00 |  |
| p | p1 | 500 | 63 | 1.050 | 3.27 | 8.927 | 12.72 | -13 | -25 | 12 | 2209.00 |  |
| p1 | p2 | 850 | 63 | 1.050 | 3.27 | 15.176 | 27.90 | -17 | -42 | 14 | 2192.00 | Tesema kare |
| p2 | p3 | 500 | 63 | 1.050 | 3.27 | 8.927 | 36.82 | -11 | -53 | 16 | 2181.00 |  |
| p3 | p4 | 350 | 63 | 1.050 | 3.27 | 6.249 | 43.07 | -20 | -73 | 30 | 2161.00 |  |
| p4 | p5 | 320 | 63 | 1.050 | 3.27 | 5.713 | 48.79 | 8 | -65 | 16 | 2169.00 |  |
| p5 | p6 | 500 | 63 | 1.050 | 3.27 | 8.927 | 57.71 | -26 | -91 | 33 | 2143.00 | Ayele mulatu |
| p6 | p7 | 650 | 63 | 1.050 | 3.27 | 11.605 | 69.32 | -55 | -146 | 77 | 2088.00 | BaShayo banato |
| p7 | p8 | 600 | 63 | 1.050 | 3.27 | 10.712 | 80.03 | 32 | -114 | 34 | 2120.00 |  |
| p8 | p9 | 650 | 63 | 1.050 | 3.27 | 11.605 | 91.63 | -55 | -169 | 77 | 2065.00 | Adela ataro |
| p9 | p10 | 750 | 63 | 1.050 | 3.27 | 13.390 | 105.02 | -15 | -184 | 79 | 2050.00 |  |
| p10 | p11 | 500 | 63 | 1.050 | 3.27 | 8.927 | 113.95 | -20 | -204 | 90 | 2030.00 |  |
| p11 | R100m3 | 510 | 63 | 1.050 | 3.27 | 9.105 | 123.06 | -7 | -211 | 88 | 2023.00 | Bedessa School |

| Altitiude of reservoir 100m3site above mean sea level= …..m+3 |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IN.pt | St.pt | Pipe L.th | P. D (mm) | Velocity (m/s) | Discharge (l/sec) | Head loss (m) | Cum. HL | rh | Cum. rH | Free Head | Node Elv. | Location |
| R | P | 150 | 75 | 1.111779 | 4.91 | 2.51998568 | 2.52 | -83 | -83 | 80.5 | 1915.0 |  |
| P | wp1 | 1050 | 38 | 0.72181 | 0.82 | 14.6751296 | 17.20 | -15 | -98 | 80.8 | 1900.0 |  |
| P | B | 100 | 50 | 0.833834 | 1.64 | 1.41749194 | 3.94 | -5 | -88 | 84.1 | 1910.0 |  |
| B | tap | 120 | 38 | 0.72181 | 0.82 | 1.67715767 | 5.61 | -10 | -98 | 92.4 | 1900.0 |  |
| B | wp5 | 1052 | 38 | 0.72181 | 0.82 | 14.7030822 | 18.64 | -5 | -93 | 74.4 | 1905.0 |  |
| P | P1 | 170 | 63 | 0.787825 | 2.45 | 1.70725862 | 4.23 | -5 | -88 | 83.8 | 1910.0 |  |
| P1 | wp2 | 50 | 38 | 0.72181 | 0.82 | 0.6988157 | 4.93 | 0 | -88 | 83.1 | 1910.0 |  |
| p1 | p2 | 850 | 50 | 0.833834 | 1.64 | 12.0486815 | 16.28 | -10 | -98 | 81.7 | 1900.0 |  |
| p2 | wp3 | 650 | 38 | 0.72181 | 0.82 | 9.08460404 | 25.36 | -10 | -108 | 82.6 | 1890.0 |  |
| p2 | wp4 | 1250 | 38 | 0.72181 | 0.82 | 17.4703924 | 33.75 | -15 | -113 | 79.3 | 1885.0 |  |
| R50m3 ww | A | 6 | 50 | 0.833834 | 1.64 | 0.08504952 | 0.09 | -4 | -4 | 3.9 | 2230.0 |  |
| A | wp6 | 50 | 38 | 0.72181 | 0.82 | 0.6988157 | 0.78 | 0 | -4 | 3.2 | 2230.0 |  |
| A | TAP | 680 | 38 | 0.72181 | 0.82 | 9.50389346 | 9.59 | -21 | -25 | 15.4 | 2209.0 |  |
| Spring | R15m3 ww | 50 | 50 | 0.416917 | 0.82 | 0.17718649 | 0.18 | -5 | -5 | 4.8 | 2235.0 |  |
| R15m3 ww | C | 50 | 63 | 0.787825 | 2.45 | 0.50213489 | 0.68 | -10 | -15 | 14.3 | 2225.0 |  |
| C | wp1sp | 50 | 38 | 0.72181 | 0.82 | 0.6988157 | 1.38 | -5 | -20 | 18.6 | 2220.0 |  |
| C | C1 | 1050 | 50 | 0.833834 | 1.64 | 14.8836654 | 15.56 | -10 | -25 | 9.4 | 2215.0 |  |
| C1 | School Tap | 120 | 38 | 0.72181 | 0.82 | 1.67715767 | 17.24 | -5 | -30 | 12.8 | 2210.0 |  |
| C1 | wp2 | 650 | 38 | 0.72181 | 0.82 | 9.08460404 | 24.65 | -15 | -40 | 15.4 | 2200.0 |  |

6.3 Inputs and Output (Possible suggested solutions)

6.3.1 Project Inputs

The project costs 11,180,128.41Eth.

6.3.2Output (Possible Suggested Solutions)

Construction of higher altitude Reservoir with a capacity of 100m3.

For the purpose of supplying potable water to the community of abaye kararo odola in the next 20years the following suggested main points and mechanisms are indicated under.

- 15m3 and 50m3 masonery reservoirs, spring caping, Anchor Blocks and that will be constructed.

- A total of nine, six faceted water points are proposed to be constructed near by the settlement area and their location is indicated on the lay out drawing.

- The required distribution pipe network and water points should be constructed as per the detail design considerations specifications and drawings.

- The management of this project should be guided and administered under kebele water supply service.

# CONCLUSION AND RECOMMENDATION

Water is a vital resource for economic and social concerns. This influential scarce resource requires intensive investment cost and appropriate management practices. From practical consideration strong management require for the sustainability of schemes.  This target groups suffers with water shortage, so basic change is required on water supply and sanitation.  As it is observed from the above computations the free head through the system is positive and it is technically feasible, and economical.

# BILL OF QUANTITIES

- Drawings